{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Sheet1","Sheet2"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":15,"n_cols":5,"rows_kept":15,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,null,null,"Steam Flow In A Pipe"]
[]
[null,"Volume:",null,0.25,"Cubic Feet of Steam per Pound"]
[]
[null,"Velocity:",null,5,"Feet per Second"]
[]
[null,"Weight of steam:",null,{"$f":"1/D5","v":4},"Per Cubic Foot"]
[]
[null,"Intenal Diameter of Pipe:",null,1,"In"]
[]
[null,"Pounds of Steam per Minute:",null,{"$f":"0.005454*D9*D11^2*D7","v":0.10908},"Pounds per Minute"]
[]
[null,"Copy Rights: Not to be copied or distributed without specific permission from Inveno Engineering LLC; kelly.paffel@invenoeng.com"]

{"sheet":"Sheet2","index":1,"n_rows":20,"n_cols":5,"rows_kept":20,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[null,null,null,"Pressure Drop"]
[]
[null,"Volume:",null,19.45,"Cubic Feet of Steam per Pound"]
[]
[null,"Length of Pipe",null,45,"Feet"]
[]
[null,"Weight of steam:",null,{"$f":"1/D6","v":5.1413881748071981E-2},"Per Cubic Foot"]
[]
[null,"Intenal Diameter of Pipe:",null,3.75,"In"]
[]
[null,"Pounds of Steam per Minute:",null,40.51,"Pounds per Minute"]
[]
[null,"Friction Factor",null,5.3E-3]
[]
[null,"Pressure drop ",null,{"$f":"(0.0484*D16*D8*D14^2)/(D12^5*D10)","v":0.49684565753682447},"Pounds per Square Inch"]
[]
[null,"Copy Rights: Not to be copied or distributed without specific permission from Inveno Engineering LLC; kelly.paffel@invenoeng.com"]