## PRV
Pressure Reducing Station Calculator
| PRESSURE REDUCING STATION 1 - 850/150 | [6 empty] | PRESSURE REDUCING STATION 2 - 850/150
[6 empty] | 603 | steam
[6 empty] | 98.4188 | water
| 66 klb/hr, 450 psig, 300 °F |  |  |  |  | 701.4188 | total | 33 klb/hr, 450 psig, 300 °F
| Subcooled | [6 empty] | Subcooled
|  |  |  | 818 °F | [6 empty] | 818 °F
| 403 klb/hr, 850 psig, 870 °F |  |  |  |  | 469 klb/hr, 150 psig, 500 °F |  | 200 klb/hr, 850 psig, 870 °F |  |  |  |  | 233 klb/hr, 150 psig, 500 °F
| Superheated |  |  |  |  | Superheated |  | Superheated |  |  |  |  | Superheated
| Inlet Steam Section | [6 empty] | Inlet Steam Section
[5 empty] | Sat. Temp | [6 empty] | Sat. Temp
| Steam Pressure : | 850 | psig |  | 527.3073 | °F |  | Steam Pressure : | 850 | psig |  | 527.3073 | °F
[5 empty] | State | [6 empty] | State
| Degree of Superheat : | 342.7 | °F |  | Superheated |  |  | Degree of Superheat : | 342.7 | °F |  | Superheated
[5 empty] | Enthalpy | [6 empty] | Enthalpy
| Temperature : | 870.0073 | °F |  | 1436.3706 | Btu/lb |  | Temperature : | 870.0073 | °F |  | 1436.3706 | Btu/lb
[5 empty] | Entropy | [6 empty] | Entropy
| Flow : | 403000 | lb/hr |  | 1.6186 | Btu/lb°F |  | Flow : | 200000 | lb/hr |  | 1.6186 | Btu/lb°F
| Desuperheating Water Section | [6 empty] | Desuperheating Water Section
[5 empty] | Sat. Temp | [6 empty] | Sat. Temp
| Water Pressure : | 450 | psig |  | 459.5615 | °F |  | Water Pressure : | 450 | psig |  | 459.5615 | °F
[5 empty] | State | [6 empty] | State
| Water Temperature : | 300 | °F |  | Subcooled |  |  | Water Temperature : | 300 | °F |  | Subcooled
[5 empty] | Enthalpy | [6 empty] | Enthalpy
| Flow Required : | 65775.7639 | lb/hr |  | 270.4906 | Btu/lb |  | Flow Required : | 32643.059 | lb/hr |  | 270.4906 | Btu/lb
|  | 142.8514 | gpm | [5 empty] | 70.894 | gpm
| Outlet Steam Section | [6 empty] | Outlet Steam Section
[5 empty] | Sat. Temp | [6 empty] | Sat. Temp
| Steam Pressure : | 150 | psig |  | 365.8723 | °F |  | Steam Pressure : | 150 | psig |  | 365.8723 | °F
[5 empty] | State | [6 empty] | State
| Degree of Superheat : | 134.1 | °F |  | Superheated |  |  | Degree of Superheat : | 134.1 | °F |  | Superheated
[5 empty] | Enthalpy | [6 empty] | Enthalpy
| Temperature : | 499.9723 | °F |  | 1272.7814 | Btu/lb |  | Temperature : | 499.9723 | °F |  | 1272.7814 | Btu/lb
| Flow : | 468775.7639 | lb/hr |  |  |  |  | Flow : | 232643.059 | lb/hr
| PRESSURE REDUCING STATION 3 - 125/50 | [6 empty] | PRESSURE REDUCING STATION 4 - 50/50
[6 empty] | 900 | steam
[6 empty] | 84.9615 | water
| 41 klb/hr, 450 psig, 300 °F |  |  |  |  | 984.9615 | total | 44 klb/hr, 450 psig, 300 °F
| Subcooled | [6 empty] | Subcooled
|  |  |  | 472 °F | [6 empty] | 481 °F
| 450 klb/hr, 125 psig, 488 °F |  |  |  |  | 491 klb/hr, 50 psig, 308 °F |  | 450 klb/hr, 50 psig, 481 °F |  |  |  |  | 494 klb/hr, 50 psig, 308 °F
| Superheated |  |  |  |  | Superheated |  | Superheated |  |  |  |  | Superheated
| Inlet Steam Section | [6 empty] | Inlet Steam Section
[5 empty] | Sat. Temp | [6 empty] | Sat. Temp
| Steam Pressure : | 125 | psig |  | 352.8705 | °F |  | Steam Pressure : | 50 | psig |  | 297.6515 | °F
[5 empty] | State | [6 empty] | State
| Degree of Superheat : | 135 | °F |  | Superheated |  |  | Degree of Superheat : | 183.3 | °F |  | Superheated
[5 empty] | Enthalpy | [6 empty] | Enthalpy
| Temperature : | 487.8705 | °F |  | 1269.0254 | Btu/lb |  | Temperature : | 480.9515 | °F |  | 1273.3367 | Btu/lb
[5 empty] | Entropy | [6 empty] | Entropy
| Flow : | 450000 | lb/hr |  | 1.6623 | Btu/lb°F |  | Flow : | 450000 | lb/hr |  | 1.7497 | Btu/lb°F
| Desuperheating Water Section | [6 empty] | Desuperheating Water Section
[5 empty] | Sat. Temp | [6 empty] | Sat. Temp
| Water Pressure : | 450 | psig |  | 459.5615 | °F |  | Water Pressure : | 450 | psig |  | 459.5615 | °F
[5 empty] | State | [6 empty] | State
| Water Temperature : | 300 | °F |  | Subcooled |  |  | Water Temperature : | 300 | °F |  | Subcooled
[5 empty] | Enthalpy | [6 empty] | Enthalpy
| Flow Required : | 41419.9008 | lb/hr |  | 270.4906 | Btu/lb |  | Flow Required : | 43541.641 | lb/hr |  | 270.4906 | Btu/lb
|  | 89.9555 | gpm | [5 empty] | 94.5635 | gpm
| Outlet Steam Section | [6 empty] | Outlet Steam Section
[5 empty] | Sat. Temp | [6 empty] | Sat. Temp
| Steam Pressure : | 50 | psig |  | 297.6515 | °F |  | Steam Pressure : | 50 | psig |  | 297.6515 | °F
[5 empty] | State | [6 empty] | State
| Degree of Superheat : | 10 | °F |  | Superheated |  |  | Degree of Superheat : | 10 | °F |  | Superheated
[5 empty] | Enthalpy | [6 empty] | Enthalpy
| Temperature : | 307.6515 | °F |  | 1184.8627 | Btu/lb |  | Temperature : | 307.6515 | °F |  | 1184.8627 | Btu/lb
| Flow : | 491419.9008 | lb/hr |  |  |  |  | Flow : | 493541.641 | lb/hr
Copy Rights: Not to be copied or distributed without specific permission from Inveno Engineering LLC; kelly.paffel@invenoeng.com
www.Invenoeng.com
Note on D29: leave it blank for saturated state
Note on D71: leave it blank for saturated state

## Turbine
Steam Turbine Calculator
This excel sheet calculates the power that turbine can generate with specific inlet and outlet conditions.
|  |  |  | Sat. Temp | [6 empty] | Shaft Energy
| Inlet Steam Pressure : | 831.2 | psig | 524.7362 | °F | Efficiency : | 1st Stage | 80 | % |  | 6.8051 | MW
State
| Degree of Superheat : | 295 | °F | Superheated |  | Efficiency : | 2nd Stage | 80 | % |  | 11.8866 | MW
Enthalpy
| Inlet Temperature : | 819.7362 | °F | 1408.0204 | Btu/lb | Efficiency : | Cond Stage | 80 | % |  | 15.0829 | MW
Entropy
| Steam Flow : | 497500 | lb/hr | 1.5991 | Btu/lb°F |  |  |  |  | Total Shaft Energy | 33.7746 | MW
current
| Outlet Steam Flow : | 156600 | lb/hr | [10 empty] | 150 | 0.31477 | 0.28445 | 0.14228 | 0.51912
|  |  |  | Sat. Temp | [9 empty] | 50 | 0.39719 | 0.5863 | 0.60942 | 0.44382
| Outlet Steam Pressure : | 141.8 | psig | 361.79 | °F | [8 empty] | cond | 0.28804 | 0.12925 | 0.2483 | 0.037059
State
| Outlet Temperature : | 473.8831 | °F | Superheated
Enthalpy (Isentropic)
| Degree of Superheat : | 112.0931 | °F | 1222.6764 | Btu/lb
Enthalpy (Actual)
| Steam Quality : | 1 |  | 1259.7452 | Btu/lb
|  |  |  | Entropy (Actual) |  |  |  | 831.2 | psig |  | 820 °F temp
|  |  |  | 1.6403 | Btu/lb°F | [5 empty] | 498 klb/hr | [5 empty] | 33.8 MW
| Outlet Steam Flow : | 197600 | lb/hr
|  |  |  | Sat. Temp | [6 empty] | 157 klb/hr | [5 empty] | 45292 hp
| Outlet Steam Pressure : | 51.5 | psig | 299.1745 | °F |  |  | 141.8 | psig |  |  |  | 198 klb/hr
State
| Outlet Temperature : | 341.5759 | °F | Superheated
Enthalpy (Isentropic)
| Degree of Superheat : | 42.4015 | °F | 1151.4483 | Btu/lb |  |  | 51.5 | psig
Enthalpy (Actual)
| Steam Quality : | 1 |  | 1202.7627 | Btu/lb | [10 empty] | -11 psig
Entropy (Actual)
|  |  |  | 1.6659 | Btu/lb°F | [10 empty] | 143 klb/hr
| Outlet Steam Flow : | 143300 | lb/hr
Sat. Temp
| Outlet Steam Pressure : | -11.1492 | psig | 148.047 | °F
State
| Outlet Temperature : | 148.047 | °F | Saturated
Enthalpy (Isentropic)
| Degree of Superheat : | 0 | °F | 959.0944 | Btu/lb
Enthalpy (Actual)
| Steam Quality : | 0.92462 |  | 1048.8796 | Btu/lb
Entropy (Actual)
|  |  |  | 1.872 | Btu/lb°F
Copy Rights: Not to be copied or distributed without specific permission from Inveno Engineering LLC; kelly.paffel@invenoeng.com
Inlet Steam Properties
Outlet Steam Properties - 1st Stage - HP to MP
Turbine Data
Outlet Steam Properties - 2nd Stage - MP to LP
Outlet Steam Properties - Cond Stage - LP to Condenser
www.Invenoeng.com
Note on D23: 0 = Liquid 0 to 1 = Saturated > 1 = Superheated
Note on D36: 0 = Liquid 0 to 1 = Saturated > 1 = Superheated
Note on D49: 0 = Liquid 0 to 1 = Saturated > 1 = Superheated

## Scenario
Scenario # | Total MW Required (MW) | Power from TG 1 | Power from TG 2 | Tie MW | Total Steam Flow Required by 150# & 50# consumer | Steam Flow to TG 1 | Steam Flow to TG 2 | Steam Flow to 850/150 PRV 1 - Old (Max Flow 403klb) | Steam Flow to 850/150 PRV 1 - New (Max Flow 200klb)
1 | 70 | 0 | 35 | 35 |  | 0 | 660

## Blank for Calculation
User Calculations Sheet
This is a blank sheet provided for the user to make notes, carry out calculations etc.
| kW | lb/hr
| 28891.3265 | 500000
| 11651.9503 | 362400
| 5345.4677 | 117600
980000
12%
117600
| flow | temp | pressure | enthalpy
TG2 | 300000 | 360 | 50 | 1212.6519
PRV | 300000 | 481 | 50 | 1273.3606
Total | 600000 | 419.8356 | 50 | 1243.0062

## Properties
Steam Tables (English Units)
Saturation properties given temperature |  |  | Saturation properties given pressure
Temperature | 50 | degF | Pressure | 12.57 | psi (a)
Saturation pressure | 0.17813 | psi (a) | Saturation temperature | 204.1778 | degF
Liquid |  |  | Liquid
Enthalpy | 18.0658 | btu/lb | Enthalpy | 172.3024 | btu/lb
Density | 62.4063 | lb /ft3 | Density | 60.0202 | lb /ft3
Entropy | 0.036086 | btu/(lb F) | Entropy | 0.30039 | btu/(lb F)
Vapour |  |  | Vapour
Vapour enthalpy | 1083.0739 | btu/lb | Vapour enthalpy | 1147.3185 | btu/lb
Vapour density | 0.00058723 | lb /ft3 | Vapour density | 0.032236 | lb /ft3
Vapour Entropy | 2.1257 | btu/(lb F) | vapour Entropy | 1.7691 | btu/(lb F)
Evaporation energy | 1065.0081 | btu/lb | Evaporation energy | 975.0161 | btu/lb
Properties given pressure and temperature |  |  | Properties given pressure and enthalpy
Pressure | 100 | psi (a) | Pressure | 12.57 | psi (a)
Temperature | 50 | degF | Enthalpy | 2788 | btu/lb
Enthalpy | 18.3543 | btu/lb | Temperature | 3074.5707 | degF
Density | 62.4269 | lb /ft3 | Density | 0.0059703 | lb /ft3
Entropy | 0.036071 | btu/(lb F) | Entropy | 2.6743 | btu/(lb F)
Vapour fraction | 0 | % | Vapour fraction | 100 | %
IF97 Region | 1 |  | IF97 Region | 2
Phase | Liquid |  | Phase | Steam
Isobaric heat capacity | 1.0015 | btu/(lb F) | Isobaric heat capacity | 0.67524 | btu/(lb F)
Speed of sound | 4752.2402 | ft/s | Speed of sound | 3414.4391 | ft/s

## Functions
Steam Tables
Temperature
Tsat_p | 14.5038 | psi |  |  | 211.2907 | deg F | Saturation temperature
T_ph | 1 | psi | 100 | btu/lb | 101.6943 | deg F | Temperture as a function of pressure and enthalpy
T_ps | 1 | psi | 1 | btu/(lb F) | 101.6943 | deg F | Temperture as a function of pressure and entropy
T_hs | 100 | btu/lb | 0.2 | btu/(lb F) | 40.7127 | deg F | Temperture as a function of enthalpy and entropy
Pressure
psat_T | 100 | deg F |  |  | 0.95044 | psi (a) | Saturation pressure
p_hs | 100 | btu/lb | 0.18513 | btu/(lb F) | 5.9883 | psi (a) | Pressure as a function of h and s.
p_hrho | 100 | btu/lb | 5 | lb/ft3 | 2.2737 | psi (a) | Pressure as a function of h and rho (density). Very unaccurate for solid water region since it's almost incompressible!
Enthalpy
hV_p | 1 | psi |  |  | 1105.4393 | btu/lb | Saturated vapour enthalpy
hL_p | 1 | psi |  |  | 69.7282 | btu/lb | Saturated liquid enthalpy
hV_T | 100 | deg F |  |  | 1104.7149 | btu/lb | Saturated vapour enthalpy
hL_T | 100 | deg F |  |  | 68.037 | btu/lb | Saturated liquid enthalpy
h_pT | 14.5038 | psi | 68 | deg F | 36.1186 | btu/lb | Entalpy as a function of pressure and temperature.
h_ps | 1 | psi | 1 | btu/(lb F) | 556.6369 | btu/lb | Entalpy as a function of pressure and entropy.
h_px | 1 | psi | 0.5 |  | 587.5838 | btu/lb | Entalpy as a function of pressure and vapour fraction
h_Tx | 100 | deg F | 0.5 |  | 586.3759 | btu/lb | Entalpy as a function of temperature and vapour fraction
h_prho | 1 | psi | 2 | lb/ft3 | 71.231 | btu/lb | Entalpy as a function of pressure and density. Observe for low temperatures (liquid) this equation has 2 solutions. (Not valid!!)
Specific volume
vV_p | 1 | psi |  |  | 333.5075 | ft3/lb | Saturated vapour volume
vL_p | 1 | psi |  |  | 0.016137 | ft3/lb | Saturated liquid volume
vV_T | 100 | deg F |  |  | 349.8696 | ft3/lb | Saturated vapour volume
vL_T | 100 | deg F |  |  | 0.016131 | ft3/lb | Saturated liquid volume
v_pT | 1 | psi | 100 | deg F | 0.016131 | ft3/lb | Specific volume as a function of pressure and temperature.
v_ph | 1 | psi | 1000 | btu/lb | 299.5568 | ft3/lb | Specific volume as a function of pressure and enthalpy
v_ps | 10 | psi | 0.18513 | btu/(lb F) | 0.016255 | ft3/lb | Specific volume as a function of pressure and entropy.
Density
rhoV_p | 1 | psi |  |  | 0.0029984 | lb/ft3 | Saturated vapour density
rhoL_p | 1 | psi |  |  | 61.9701 | lb/ft3 | Saturated liquid density
rhoV_T | 100 | deg F |  |  | 0.0028582 | lb/ft3 | Saturated vapour density
rhoL_T | 100 | deg F |  |  | 61.9918 | lb/ft3 | Saturated liquid density
rho_pT | 1 | psi | 100 | deg F | 61.9918 | lb/ft3 | Density as a function of pressure and temperature.
rho_ph | 1 | psi | 1000 | btu/lb | 0.0033383 | lb/ft3 | Density as a function of pressure and enthalpy
rho_ps | 1 | psi | 1 | btu/(lb F) | 0.0063777 | lb/ft3 | Density as a function of pressure and entropy.
Specific entropy
sV_p | 1 | psi |  |  | 1.9776 | btu/(lb F) | Saturated vapour entropy
sL_p | 1 | psi |  |  | 0.13263 | btu/(lb F) | Saturated liquid entropy
sV_T | 50 | deg F |  |  | 2.1257 | btu/(lb F) | Saturated vapour entropy
sL_T | 100 | deg F |  |  | 0.12961 | btu/(lb F) | Saturated liquid entropy
s_pT | 1 | psi | 50 | deg F | 0.036086 | btu/(lb F) | Specific entropy as a function of pressure and temperature (Returns saturated vapour entalpy if mixture.)
s_ph | 10 | psi | 100 | btu/lb | 0.18513 | btu/(lb F) | Specific entropy as a function of pressure and enthalpy
Specific internal energy
uV_p | 1 | psi |  |  | 1043.7239 | btu/lb | Saturated vapour internal energy
uL_p | 1 | psi |  |  | 69.7253 | btu/lb | Saturated liquid internal energy
uV_T | 100 | deg F |  |  | 1043.1803 | btu/lb | Saturated vapour internal energy
uL_T | 100 | deg F |  |  | 68.0341 | btu/lb | Saturated liquid internal energy
u_pT | 1 | psi | 100 | deg F | 68.0341 | btu/lb | Specific internal energy as a function of pressure and temperature.
u_ph | 1 | psi | 1000 | btu/lb | 944.5671 | btu/lb | Specific internal energy as a function of pressure and enthalpy
u_ps | 1 | psi | 1 | btu/(lb F) | 527.6216 | btu/lb | Specific internal energy as a function of pressure and entropy.
Specific isobaric heat capacity
CpV_p | 1 | psi |  |  | 0.46105 | btu/(lb F) | Saturated vapour heat capacity
CpL_p | 1 | psi |  |  | 0.9981 | btu/(lb F) | Saturated liquid heat capacity
CpV_T | 100 | deg F |  |  | 0.46071 | btu/(lb F) | Saturated vapour heat capacity
CpL_T | 100 | deg F |  |  | 0.99811 | btu/(lb F) | Saturated liquid heat capacity
Cp_pT | 1 | psi | 100 | deg F | 0.99811 | btu/(lb F) | Specific isobaric heat capacity as a function of pressure and temperature.
Cp_ph | 100 | psi | 200 | btu/lb | 1.0104 | btu/(lb F) | Specific isobaric heat capacity as a function of pressure and enthalpy
Cp_ps | 100 | psi | 0.18513 | btu/(lb F) | 0.99832 | btu/(lb F) | Specific isobaric heat capacity as a function of pressure and entropy.
Specific isochoric heat capacity
CvV_p | 1 | psi |  |  | 0.34738 | btu/(lb F) | Saturated vapour isochoric heat capacity
CvL_p | 1 | psi |  |  | 0.97419 | btu/(lb F) | Saturated liquid isochoric heat capacity
CvV_T | 100 | deg F |  |  | 0.34713 | btu/(lb F) | Saturated vapour isochoric heat capacity
CvL_T | 100 | deg F |  |  | 0.97524 | btu/(lb F) | Saturated liquid isochoric heat capacity
Cv_pT | 1 | psi | 100 | deg F | 0.97524 | btu/(lb F) | Specific isochoric heat capacity as a function of pressure and temperature.
Cv_ph | 100 | psi | 200 | btu/lb | 0.88674 | btu/(lb F) | Specific isochoric heat capacity as a function of pressure and enthalpy
Cv_ps | 100 | psi | 0.18513 | btu/(lb F) | 0.95412 | btu/(lb F) | Specific isochoric heat capacity as a function of pressure and entropy.
Speed of sound
wV_p | 1 | psi |  |  | 1430.0233 | ft/s | Saturated vapour speed of sound
wL_p | 1 | psi |  |  | 5016.1266 | ft/s | Saturated liquid speed of sound
wV_T | 100 | deg F |  |  | 1427.9807 | ft/s | Saturated vapour speed of sound
wL_T | 100 | deg F |  |  | 5010.5241 | ft/s | Saturated liquid speed of sound
w_pT | 1 | psi | 100 | deg F | 5010.5259 | ft/s | Speed of sound as a function of pressure and temperature.
w_ph | 100 | psi | 100 | btu/lb | 5090.5178 | ft/s | Speed of sound as a function of pressure and enthalpy
w_ps | 100 | psi | 0.18513 | btu/(lb F) | 5090.9194 | ft/s | Speed of sound as a function of pressure and entropy.
Dynamic Viscosity
Viscosity is not part of IAPWS Steam IF97. Equations from ""Revised Release on the IAPWS Formulation 1985 for the Viscosity of Ordinary Water Substance"", 2003 are used.
Viscosity in the mixed region (4) is interpolated according to the density. This is not true since it will be two fases.
my_pT | 1 | psi | 100 | deg F | 1.6478 | lb/ft/hr | Viscosity as a function of pressure and temperature.
my_ph | 100 | psi | 100 | btu/lb | 1.2111 | lb/ft/hr | Viscosity as a function of pressure and enthalpy
my_ps | 100 | psi | 0.18513 | btu/(lb F) | 1.2082 | lb/ft/hr | Viscosity as a function of pressure and entropy.
Prandtl
Calcualted as Cp*my/tc
pr_pT | 1 | psi | 200 | deg F | 0.97012 | -
pr_ph | 1 | psi | 0.19 | btu/lb | 13.4056 | -
Thermal Conductivity
Revised release on the IAPS Formulation 1985 for the Thermal Conductivity of ordinary water substance (IAPWS 1998)
tcL_p | 1 | psi |  |  | 0.36223 | btu/(h*ft*F) | Saturated vapour thermal conductivity
tcV_p | 1 | psi |  |  | 0.011198 | btu/(h*ft*F) | Saturated liquid thermal conductivity
tcL_T | 50 | deg F |  |  | 0.33623 | btu/(h*ft*F) | Saturated vapour thermal conductivity
tcV_T | 50 | deg F |  |  | 0.0099464 | btu/(h*ft*F) | Saturated liquid thermal conductivity
tc_pT | 1 | psi | 50 | deg F | 0.33623 | btu/(h*ft*F) | Thermal conductivity as a function of pressure and temperature.
tc_ph | 1 | psi | 100 | btu/(lb F) | 0.020137 | btu/(h*ft*F) | Thermal conductivity as a function of pressure and enthalpy
tc_hs | 100 | btu/lb | 0.18513 | btu/(lb F) | 0.37348 | btu/(h*ft*F) | Thermal conductivity as a function of enthalpy and entropy
Surface Tension
IAPWS Release on Surface Tension of Ordinary Water Substance, September 1994
st_T | 100 | deg F |  |  | 0.0053423 | lb/ft | Surface tension for two phase water/steam as a function of T
st_p | 1 | psi |  |  | 0.0047831 | lb/ft | Surface tension for two phase water/steam as a function of T
Vapour fraction
x_ph | 1 | psi | 1000 | btu/lb | 0.8982 |  | Vapour fraction as a function of pressure and enthalpy
x_ps | 1 | psi | 4 | btu/(lb F) | 1 |  | Vapour fraction as a function of pressure and entropy.
Vapour Volume Fraction
Observe that vapour volume fraction is very sensitive. Vapour volume is about 1000 times greater than liquid volume and therfore vapour volume fraction
gets close to the accurancy of steam IF-97
vx_ph | 1 | psi | 418 | btu/lb | 0.9999 |  | Vapour volume fraction as a function of pressure and enthalpy
vx_ps | 1 | psi | 4 | btu/(lb F) | 1 |  | Vapour volume fraction as a function of pressure and entropy.