## Main
Buried Uninsulated Pipe Energy Loss Calculator
Single Pipe (assumed no other pipes or thermal anomalies are within close proximity)
Abbreviations:
| Thermal resistance of soil | Rs | h-ft-F/Btu
| Thermal conductivity of soil | ks | Btu/h-ft-F
| Burial depth of centerline | d | ft
| Outer radius of pipe | ro | ft
Soil Thermal Conductivities
| Soil Moisture Content |  | Thermal Conductivity, Btu/h-ft-F
| (by mass) |  | Sand | Silt | Clay
| Low, < 4% |  | 0.17 | 0.08 | 0.08
| Medium 4 to 20% |  | 1.08 | 0.75 | 0.58
| High, > 20% |  | 1.25 | 1.25 | 1.25
Chyu et al. (1997a,b; 1998a,b)
Pipe Properties
| Inner diameter |  | 10.02 | in |  |  | d = | 6 ft
| Wall thickness |  | 0.365 | in
| Outer radius, ro |  | 0.44792 | ft
| Depth to centerline of pipe, d |  | 6 | ft |  |  | ro = | 0.45 ft
| d/ro ratio |  | 13.3953 | ratio > 4 |  |  | ri = | 0.42 ft
Soil Properties
| Thermal Conductivity, ks |  | 1 | Btu/h-Ft-F |  | Formula from ASHRAE Handbook
| Thermal Resistance, Rs |  | 0.52331 | h-ft-F/Btu
| Soil Temperature |  | 60 | °F
Others
| Fluid Temperature |  | 325 | °F
| Heat Loss per Unit Length of System, q |  | 506.3918 | Btu/h-ft
Monetary Measurement
| Operational days |  | 365 | days per year
| Length of Pipe System |  | 1988 | ft
| Latent Energy in Fluid |  | 868 | Btu/lb
| Total Energy Loss in System |  | 1.0067 | MMBtu/h
|  |  | 1.1598 | 1,000 lb/h
|  |  | 10.1599 | million lbs per year
| Cost of Steam |  | 6.42 | per 1,000 lbs of steam
| Monetary Loss |  | 65226.2625 | per year
Copy Rights: Not to be copied or distributed without specific permission from Inveno Engineering LLC; kelly.paffel@invenoeng.com
`
Earth
ro
ri
Not drawn to scale
www.Invenoeng.com